**Electric League Code Meeting, Wednesday, July 15**

Code Changes to be discussed. The interest is in what how the AHJ is interpreting the code changes and what additional documentation will be required.

1. 210.8 listing significant changes that will now require GFCI
2. 230.67 Surge Protection for dwelling units. In multifamily applications. (Jimmy’s understanding is that we can have a surge protection device in the main switchboard which feeds the group metering to comply. We do not need an SPD in each tenant panel.)
3. 230.71 Maximum number of Disconnects. This will have a significant impact to equipment footprints.
4. 240.67 Arc Energy reduction methods for Fuses. (This has been in effect since January 1st, 2020.)
5. Additional verbiage in 240.67 and 240.87 regarding documentation requirement and Performance Testing
	1. Documentation = Arc Flash Study?
	2. Performance Testing = Deferring this to the manufacturers to prove our method of mitigation is acceptable?